## PART 1	GENERAL

- 1.1	SUMMARY

- A.	This section includes vertical condensing hot water boiler(s) for indoor space-heating application.

- 1.2	REFERENCES

Intertek (ETL)

      - ETL certified to ANSI Z21.13/CSA 4.9, latest edition

American Society of Mechanical Engineers:

      - ASME Section IV - Boiler and Pressure Vessel Code - Heating Boilers

American Society of Heating, Refrigeration and Air Conditioning Engineers

      - ASHRAE: Standard 90.1 Energy Standard for Buildings

American National Standards Institute:

      - ANSI Z21.13 / CSA 4.9 latest edition – Gas Fired Low Pressure Steam and Hot Water Boilers

Air Conditioning, Heating and Refrigeration Institute (AHRI):

      - Heating Capacity, MBH – DOE 10 CFR Part 430

      - Annual Fuel Utilization Efficiency (AFUE), % - DOE 10CFR Part 430

National Fire Protection Association:

      - NFPA 54 - National Fuel Gas Code (ANSI Z223.1)

Relevant local and/or project specific Codes and Standards

- 1.3	SUBMITTALS

    - In accordance with Contract Documents. Minimum product data to include:

Capacities, accessories and options included with boiler.

General layout, dimensions, size and location of all required connections.

Electrical characteristics

Weight and mounting loads.

Manufacturer’s installation and start-up instructions.

Equipment Operation and Maintenance Manuals.

- 1.4	QUALITY ASSURANCE

    - Use an adequate number of skilled workers, trained and experienced in the necessary crafts, and who are completely familiar with the specified requirements, pertinent contract documents, and methods needed for proper performance of the work described therein.

Provide the services of a manufacturer’s factory-authorized representative to inspect and verify proper installation of this equipment, and to provide equipment start-up and operator training.

- 1.5	DELIVERY, STORAGE, AND HANDLING

    - In accordance with Contract Documents.

Accept equipment and accessories in Factory shipping packaging. Inspect for damage. Keep boiler in a vertical position from time of delivery to final installation.

While stored, all equipment must be protected from external elements such as inclement weather, job site construction activity, etc. Protect equipment from damage by leaving packaging in place until installation.

- 1.6	WARRANTY

    - See Warranty Sheet for U.S. Boiler Company Water and Steam Boilers.

## PART 2	PRODUCTS

2.1	ACCEPTABLE MANUFACTURERS

- US Boiler Company, Inc. Alpine Condensing Boiler, Model ALP [080, 105, 150, 210, 285].  Refer to the Equipment Schedule in the Contract Drawings for the specific design and performance criteria.

- It shall be the responsibility of the Contractor to insure that any substituted equipment is equivalent in fit, form and function to the specified equipment. The cost of any additional work caused by the substitution of equipment shall be borne by the Contractor.

2.2	GENERAL REQUIREMENTS

- Boiler

  - The boiler shall be assembled, firetested and shipped as a factory-packaged unit, complete with jacket, gas manifold, burner and controls mounted & wired, with boiler connections specified in this Section.

  - The boiler shall be constructed in conformance to ASME Section IV and ANSI Z21.13. The boiler shall bear the ASME “H” stamp with a maximum allowable working pressure (MAWP) of 160 PSI.  Pressure vessel shall be subjected to a hydrostatic pressure test of 240 PSIG at the factory before shipment.

  - The boiler shall be an ultra-high efficiency-condensing boiler with a pressure vessel, constructed of stainless steel, which shall not require a refractory combustion chamber.

  - The boiler shall be equipped with an integral pre-mix, metal-mesh type forced draft burner incorporating full modulation with 5:1 turndown.

  - The boiler gas valve will be designed with zero pressure regulation and equipped with a variable speed blower system to precisely control the fuel/air mixture, providing fully modulating firing rates for maximum efficiency.

      - All piping and wiring connections shall be located on the left side of the boiler. Connections include: supply / return water connections, relief / drain tapping, condensate trap drain, and gas valve inlet connection. Condensate trap shall have a factory supplied compression fitting. A factory supplied drain valve and oversized relief valve shall be provided with the boiler(s).

The flue passages and combustion chamber shall be accessible from the front of the boiler for cleaning.

The boiler shall be provided with a heavy-duty 20 gauge steel jacket with a rust resistant powder coat finish. Jackets made of plastic or resin material shall not be acceptable. The boiler jacket shall contain an internal electrical cabinet for power and limit circuit wiring, providing a clean finished look when the jacket is installed. Furthermore, all electrical and control components shall be mounted on a pullout-tray, providing easy access to wiring terminals, controls and 360 view of all wiring components. Individual lift-off jacket front panel may be installed after system piping and wiring to allow ease of access to the pressure vessel.

The electrical components shall be separated from incoming combustion air gas, which may contain excess humidity, dust and other contaminants brought through ducted combustion air.

A polypropylene condensate trap with a float-actuated shut-off switch shall be located within the boiler jacket and beneath the heat exchanger drain pan. The float-actuated shutoff switch must be located upstream from any bends in the condensate trap. Float switches located on the downstream side of the condensate trap shall not be acceptable due to the possibility of blockages occurring in the trap bends.

The float-actuated switch shall be offset from the condensate drip to prevent mineral build-up from interfering with the switch actuation.

Boiler Control System

- Scope of Supply 
Supply a Boiler Control System to provide safety interlocks and water temperature control. The control system shall be fully integrated into the boiler control cabinet and incorporate single and multiple boiler control logic, inputs, outputs and communication interfaces. The control system shall coordinate the operation of up to eight (8) fully modulating hot water boilers and circulation pumps. The control system shall simply control boiler modulation and on/off outputs based on the boiler water supply temperature and an operator-adjusted setpoint. However, using parameter menu selections, the control system shall allow the boiler to respond to remote system water temperature and outside air temperatures with domestic hot water priority (DHWP) and warm weather shut down (WWSD) or building automation system (BAS) firing rate demand, remote setpoint or remote start/stop commands.

- Boiler Control
Using PID (proportional-integral-derivative) based control the remote system water temperature shall be compared with a setpoint to establish a target boiler firing rate. If the secondary loop flow speed is greater than the primary loop flow speed, firing rate is increased in response to the decrease in secondary loop temperature. When the remote system temperature is near the boiler high limit temperature, the boiler supply sensor shall limit the maximum boiler supply temperature to prevent boiler high limit events. Alternately, using parameter menu selections, the control system shall allow the boiler to respond directly to boiler supply temperature and setpoint to establish a target boiler-firing rate while remote system water temperature is used for display purposes only. Each boiler’s fuel flow control valve shall be mechanically linked to the airflow control device to assure an air rich fuel/air ratio. All the automated logic is required to ensure that pre-purge, post-purge, light off, and burner modulation shall be provided.

- Hot Water Temperature Setpoint
When the controller is in the local control mode, the control system shall establish the setpoint based on outside air temperature and a reset function curve, or be manually adjusted by the operator. When enabled, the setpoint shall be adjusted above a preset minimum setpoint upon sensing a domestic hot water demand contact input. When in remote mode, the control system shall accept a Modbus or 4-20mAdc remote setpoint or firing rate demand signal from an external BAS.

- Multiple Boiler Sequence
Multiple boilers shall be modulated in “Unison” (all at the same firing rate).  The control system shall utilize both water temperature and boiler firing rate percent to start and stop the boilers and shall minimize the total number of boilers in operation. The control system shall start and stop boilers when the water temperature is outside the adjustable temperature limit for longer than the adjustable time delay. In order to minimize temperature deviations, the control system shall start and stop the next boiler when the “lead” boiler is at an adjustable firing rate limit for longer than the adjustable time delay. The control system shall monitor both boiler lockout and limit circuits to automatically skip over those boilers that are powered down for maintenance, tripped or otherwise will not start. The boiler shall be run at low fire for warm-up for a preset low fire hold time. When enabled, warm weather shut down control logic shall prevent boiler operation. The controller shall also be capable of auto-rotation of the boilers based on user-selected run time hours.

- User Interface
A touch screen message display shall be provided to display numeric data, startup and shutdown sequence status, alarm, system diagnostic, first-out messages and boiler historical information. In the event of a fault condition, the display shall provide help screens to determine the cause of the problem and corrective actions. Historical information shall include graphical trends, lockout history, boiler & circulator cycle counts and run time hours

- Circulator Control
The controller shall be capable of sequencing the boiler, domestic hot water or system circulators.  Simple parameter selections shall allow all three pumps to respond properly to various hydronic piping arrangements including either a boiler or primary piped indirect water heater. The controller shall perform circulator exercise to help prevent pump rotor seizing.

- 7.	Communication
The control includes state-of-the-art modulating lead-lag sequencer for up to eight (8) boilers capable of auto rotation, outdoor reset, and peer-to-peer communication. The peer-peer network is truly “plug and play”. Communication is activated by simply connecting a RJ45 ethernet cable between boilers. The control provides precise boiler coordination by sequencing boilers based on both header water temperature and boiler modulation rate. A factory configured RS485 Modbus interface is available for Energy Management System (EMS) monitoring when not used for Multiple Boiler Sequencer Peer-To-Peer Network.

- Quality Assurance
The boiler control system shall be supplied as part of a factory-assembled and tested burner control cabinet.

- B.	Boiler Trim

- Combination pressure-temperature gauge, 2-1/2 inch diameter.

      - Supply and return temperature sensors - shall be mounted on the supply and return connections inside the boiler jacket. Each sensor shall be accessible through a removable boiler front door. The boiler control shall measure supply and return temperatures and notify the operator if the direction of flow is reversed.

The boiler control shall adjust to impending temperature changes in such a way to minimize fuel consumption and maximize efficiency. The control shall measure temperatures and the rate of change in those temperatures and respond early, rather than waiting for temperatures to exceed limit control settings.

      - Outdoor air temperature sensor, if required, to automatically adjust the modulation rate setpoint on the boiler according to the outdoor temperature to optimize boiler operation and efficiency.

      - Flue gas temperature sensor shall be mounted in the flue vent connector to monitor flue gas temperatures and reduce the blower speed when flue gas temperatures exceed 184°F.  If the flue temperatures exceed 194°F, forced boilers recycle results.

      - ASME Section IV safety relief valve sized to exceed the heating capacity of the boiler, which shall be factory set to relieve pressure at [30 PSI – 080 thru 285; 50, 80 & 100PSI Optional for All Sizes] water working pressure.

Air vent valve shall be included to release trapped air inside the boiler’s heat exchanger.

Drain valve, 3/4 inch.

Low water cutoff (LWCO) device with automatic reset (optional).

- E.	Vent & Intake Air Connections

- The vent system shall be in accordance with National Fuel Code, NFPA 54/ANSI Z221.3 or CAN/CSA B149.1 Installation Code for Canada, or, applicable provisions of local building codes.

- The boiler shall be vented using PVC/CPVC vent material in accordance with local code. A Factory supplied 90º elbow (schedule 80 CPVC) and a 30-inch length of schedule 40 CPVC pipe must be included as a transition from the boiler to traditional solid core schedule 40 PVC vent material. Foam core pipe shall not be an approved vent material for either intake/exhaust piping. Vent connections must be located at the rear of the boiler.  (NOTE TO SPECIFIER:  Other venting options available.  Please contact your local factory representative for details or consult the Alpine Installation, Operating and Service Instructions)

- Air intake piping shall be PVC that is sealed and pressure tight. Pipe must be at least the same size as the inlet air connection on the boiler. (NOTE TO SPECIFIER:  Other air intake options available.  Please contact your local factory representative for details or consult the Alpine Installation, Operating and Service Instructions)

2.3	PERFORMANCE

- Boiler efficiency shall be as stated in the Equipment Schedule of the Contract Documents.

- The burner shall emit no more than 20 ppm NOx and 50 ppm CO (corrected to 3% O2) at all firing rates.

- Provide services of a manufacturer's authorized representative to perform combustion test including boiler firing rate, gas flow rate, heat input, burner manifold gas pressure, percent carbon monoxide, percent oxygen, percent excess air, flue gas temperature at outlet, ambient temperature, net stack temperature, percent stack loss, percent combustion efficiency, and heat output.  Perform test at minimum, mid-range, and high fire.

## PART 3	EXECUTION

- 3.1	INSTALLATION

- In accordance with Contract Documents and boiler manufacturer's printed instructions.

- Flush and clean the boiler upon completion of installation in accordance with manufacturer's start-up instructions. The boiler must be isolated when any cleaning or testing of system piping is being performed.

- Install skid plumb and level, to plus or minus 1/16 inch over base.

- Maintain manufacturer's recommended clearances around and over equipment, and as required by local Code.

- Arrange all electrical conduit, piping, exhaust vent, and air intake with clearances for burner removal and service of all equipment.

- Connect exhaust vent to boiler vent connection.

- If shown in Contract Drawings, connect full sized air inlet vent to flanged connector on boiler.

- Connect fuel piping in accordance with NFPA 54. Pipe size to be the same, or greater, than the gas train inlet connection.

- Use full size (minimum) pipe/tubing on all gas vent connections.

- Connect water piping, full size, to supply and return connections.

- Install all piping accessories per the details on the contract drawings.

- Install discharge piping from relief valves (open termination for viewing) and all drains to nearest floor drain.

- Provide necessary water treatment to satisfy manufacturer’s specified water quality limits.

- END OF SECTION