Specification Rev. 04/24/2020

Intelligent Zone Control

(with boiler integration)

U.S. Boiler Company

P.O.Box 3020 Lancaster, Pennsylvania 17604-3020

Phone: 888-432-8887

www.usboiler.net

- DESCRIPTION

  - Zone Control, Circulator or Valve Panel. This device shall provide zone control power switching capability between boilers and multiple-zone circulators or valves.

  - The Zone Control shall provide special zone management capability when zoned systems are connected to selected high-efficiency boilers from U.S. Boiler Company equipped with HeatMatching™ software. It shall evaluate individual zone heat demands and optimize boiler modulation, starting at low firing rates, to meet these demands.

- SOURCING

  - Supplier shall be: U.S. Boiler Company, Lancaster, PA

  - The installed product shall be a Sage Zone Control              (Select Model-number from right): “Circulator Panel- 104590-01”, and/or “Valve Panel- 105589-01.”

- FUNCTIONS

  - Boiler Connection, Plug-and-play- The Zone Control shall communicate to selected boilers with EnviraCOM communications using a nine foot CAT 5, 8 position modular I/O cable included with each zone control.  This shall make end switches and ZR/ZC terminals available for other functions.

  - Boiler Communications and User interface- The Zone Control shall communicate with touch screen control panels on selected high efficiency condensing boilers from U.S. Boiler Company. These touch screen controls shall allow access and custom adjustments to zone management functions and provide BTU monitoring and zone cycle history.

  - Three Temperature System- The Zone Control shall support the three temperature demands found in most contemporary, residential hydronic heating systems.

    - “Central Heat” supports standard radiation heating

    - “Domestic” supports domestic hot water heating.

    - “Auxiliary Heat” demand is a second heating demand that may be used to serve either low temperature radiation or warmer heat demands such as fan coils.

  - HeatMatchTM Software compatibility- The Zone Control shall function with HeatMatching Software on selected high efficiency boilers from U.S. Boiler Company using default-settings or field-settings to “size” the boiler to match active (turned on)   zones. It will measure water temperature and fire the boiler only as needed for the zone BTU demand. This reduces run times, increases operating efficiency, and reduces excessive cycling to extend boiler and system life.

  - Whole Home Freeze Protection when enabled- When a boiler outdoor sensor detects outside temperature that is below freezing and an individual zone that has not opened for over an hour, the primary circulators shall operate for a short period to move water past the boiler supply sensor and warm the zone with circulated water from other parts of the building.

  - The Zone Control shall also include these additional features and functions:

    - Selectable “Primary Circulator Run”

    - Priority Protection

    - DHW Post Purge

    - Circulator Exercise

    - Front External Indicator Lights

    - Sealed Relays

    - Fuse Protection

    - Expandable to 4 Zoning Controls  (16 zones with 4 zone controls)

    - Universal Thermostat Compatibility

    - End Switches (dry contacts)

    - 100% Factory Tested - UL Approved

- OTHER TECHNICAL SPECIFICATIONS AND REQUIREMENTS

  - The installed Sage Zone Control                (Select “Circulator Panel” or “Valve Panel” from left column below) shall comply with the corresponding electrical and physical specifications shown in the table and bullet notes below.